## HO meter
Insertion meter sizing program
Date: | 2006-01-10 13:44 | [8 empty] | Hoffer Flow Controls, Inc.
Customer: | [9 empty] | Rev 1.02
Reference:
|  | Meter |  | Min | Min
|  | max | % of | velocity | velocity |  | Min flow | Min flow | Max
Meter | Blade | velocity | max | MAG coil | MCP coil | Status | MAG coil | MCP coil | flow
size | angle | FPS | flow | FPS | FPS |  | ACFM | ACFM | ACFM
1.5" | 15 | 212.7028
1.5" | 20 | 155.982
1.5" | 25 | 121.7723
1.5" | 30 | 98.375
2" | 15 | 199.5608
2" | 20 | 146.6772
2" | 25 | 114.7475
2" | 30 | 92.4964
Calculation notes: Densitry at STP (70F, 14.7psi) is listed in the fluid table located at A41:H67. Density range is calculated based on density at STP, and max /min values of T & P: Dmin = Density * 36 * Pmin / Tmax Dmax = Density * 36 * Pmax / Tmin Required min/max velocity is calculated from required flow rate and pipe size: Vmin = Fmin / Pipe / 60 Vmax = Fmax / Pipe / 60 Max velocity is a constant for each meter. It is calculated based on meter max flow rate (ACFM) and meter cross section area in table located at A70:I80. Min velocity is calculated based on meter min flow rate at density of 0.1 derived from HO meter sizing program, and square root of ratio of densities (0.1 to min flowing density)

## Data
Gas | Symbol | Density | SG | UGASconst |  | Temperature | Pressure | Flow |  |  |  | Temp_Rankine | Press_PSIA | Description
Acetylene | C2H2 | 0.06914 | 0.9057 | 59.4 |  | Fahrenheit | PSIG | ACFM |  |  |  | 518.67 | 14.6959 | OIML : 15 C 101.325 KPa
Air |  | 0.075188 | 1 | 53.9 |  | Rankine | PSIA | SCFM |  |  |  | 529.47 | 14.6959 | USA : 70 F 14.7 PSIA
Ammonia | NH3 | 0.04425 | 0.597 | 90.8 |  | Celsius | BarG | Lbs/min |  |  |  | 540.27 | 14.6959 | ASIAN : 27 C 101.325 KPa
Argon | AR | 0.10341 | 1.38 | 38.7 |  | Kelvin | BarA | Kg/min |  |  |  | 518.67 | 14.5038 | PTB : 15 C 1 Bar
Butene | C4H10 | 0.15626 | 2.076 | 0 |  |  | kg/cm^2 | AM3/min |  |  |  | 545.67 | 14.6959 | SIRIM : 30 C 101.325 KPa
Carbon dioxide | CO2 | 0.1142 | 1.521 | 35.1 |  |  | Pascals | NM3/min |  |  |  | 491.67 | 14.6959 | Normal: 0 C 101.325 Kpa
Carbon monoxide | CO | 0.07236 | 0.9678 | 55.2 |  |  | KPaG | ALPM |  |  |  | 0 | 0 | USER specified.
Carbon tetra floride | CF4 | 0.22727 | 3.0227 | 0 |  |  | MPaG | NLPM
Ethane | C2H6 | 0.078125 | 1.047 | 0 |  |  | ATM | ACFH
Ethylene | C4H4 | 0.072464 | 0.974 | 0 |  |  | KPa | SCFH
Freon R12 | CCL2F2 | 0.3193 | 4.2 | 0 |  |  | MPa | Lbs/hr
Freon R22 | CHCIF2 | 0.2273 | 0 | 0 |  |  |  | Kg/hr
Fluorine | F2 | 0.09804 | 1.696 | 0 |  |  |  | AM3/hr
Helium | HE | 0.010352 | 0.137 | 386 |  |  |  | NM3/hr
Hydrogen | H2 | 0.005217 | 0.06952 | 767 |  |  |  | ALPH
Krypton | KR | 0.2169 | 2.818 | 0 |  |  |  | NLPH
Methane | CH4 | 0.042184 | 0.5549 | 96.4
Natural gas |  | 0.04494 | 0.5977 | 0
Neon | NE | 0.052192 | 0.6941 | 0
Nitrogen | N2 | 0.07236 | 0.9624 | 55.2
Nitrous Oxide | N2O | 0.11494 | 1.53 | 0
Oxygen | O2 | 0.082645 | 1.0992 | 48.3
Propane | C3H8 | 0.11765 | 1.5503 | 0
Propylene | C3H6 | 0.11038 | 1.476 | 0
Sulfer dioxide | SO2 | 0.16573 | 2.264 | 24.1
User Defined |  | 0 | 0 | 0
Meter | Flow1 | Flow2 | Flow3 | Flow4 | Flow5 | MAG | MCP | Drop1 | Drop2 | Drop3 | Drop4
size | 15 | 20 | 25 | 30 | 1 | 0 | 0 | 15 | 20 | 25 | 30
MF30 | 0.05 | 0 | 0 | 0 | 3333 | 0 | 0.005 | 0 | 0 | 0 | 2
MF50 | 0.1 | 0 | 0 | 0 | 3333 | 0 | 0.01 | 0 | 0 | 0 | 2
MF80 | 0.2 | 0 | 0 | 0 | 3333 | 0 | 0.02 | 0 | 0 | 0 | 2
MF90 | 0.3 | 0 | 0 | 0 | 3333 | 0 | 0.03 | 0 | 0 | 0 | 2
M125 | 0.5 | 0 | 0 | 0 | 3333 | 0 | 0.05 | 0 | 0 | 0 | 2
M175 | 1 | 0 | 0 | 0 | 3333 | 0 | 0.1 | 0 | 0 | 0 | 2
1/4 | 3.47 | 2.55 | 1.99 | 1.61 | 2500 | 0 | 0.15 | 0.4 | 0.7 | 1 | 2
3/8 | 5 | 3.68 | 2.88 | 2.32 | 2500 | 0 | 0.3 | 0.4 | 0.6 | 0.9 | 2
5/8 | 9.5 | 6.95 | 5.43 | 4.39 | 2500 | 0 | 0.5 | 0.5 | 0.7 | 1 | 2
3/4 | 20 | 14.7 | 11.5 | 9.2 | 2500 | 0 | 0.6 | 0.4 | 0.5 | 1 | 2
1 | 43 | 32 | 25 | 20 | 2080 | 2.5 | 0.8 | 0.8 | 1.5 | 2 | 4
1.25 | 100 | 74.7 | 57 | 47 | 2500 | 3.5 | 1.25 | 0.8 | 1.5 | 2.5 | 4
1.5 | 120 | 88 | 68.7 | 55.5 | 1800 | 5 | 1.75 | 0.7 | 1 | 1.8 | 3
2 | 200 | 147 | 115 | 92.7 | 1600 | 10 | 3.5 | 1.25 | 1.5 | 3 | 6
2.5 | 522 | 384 | 300 | 242 | 2400 | 15 | 5 | 2 | 3 | 5 | 8
3 | 782 | 576 | 449 | 363 | 1575 | 20 | 7.5 | 2 | 3 | 5 | 8
4 | 1100 | 809 | 632 | 510 | 1260 | 30 | 0 | 1.5 | 2.25 | 4 | 8
5 | 2149 | 1582 | 1235 | 997 | 945 | 40 | 0 | 2 | 2.5 | 3 | 8
6 | 3321 | 2445 | 1908 | 1541 | 945 | 50 | 0 | 1.8 | 3.5 | 5 | 8
8 | 4800 | 3530 | 2760 | 2230 | 504 | 100 | 0 | 1.7 | 2.5 | 5 | 8
10 | 7500 | 5520 | 4310 | 3480 | 487 | 150 | 0 | 1.5 | 2.25 | 4 | 8
12 | 12000 | 8830 | 6800 | 5570 | 478 | 200 | 0 | 1.5 | 2.5 | 4 | 8
Min and Max velocity at air density 0.1 Lb/ft3
Meter size | Blade angle | Max flow ACFM | Min flow MAG coil ACFM | Min flow MCP coil ACFM | Cross section area (ft2) | Maximum Velocity FPS | Minimum Velocity MAG coil FPS | Minimum Velocity MCP coil FPS
1.5" | 15 | 120 | 15.8 | 5.53 | 0.0094028 | 212.7028 | 28.0059 | 9.8021
1.5" | 20 | 88 | 11.63 | 4.07 | 0.0094028 | 155.982 | 20.6144 | 7.2142
1.5" | 25 | 68.7 | 9.08 | 3.18 | 0.0094028 | 121.7723 | 16.0945 | 5.6366
1.5" | 30 | 55.5 | 7.33 | 2.57 | 0.0094028 | 98.375 | 12.9926 | 4.5554
2" | 15 | 200 | 31.6 | 11.06 | 0.016703 | 199.5608 | 31.5306 | 11.0357
2" | 20 | 147 | 23.26 | 8.14 | 0.016703 | 146.6772 | 23.2089 | 8.1221
2" | 25 | 115 | 18.16 | 6.36 | 0.016703 | 114.7475 | 18.1201 | 6.346
2" | 30 | 92.7 | 14.67 | 5.13 | 0.016703 | 92.4964 | 14.6378 | 5.1187
| Inside dia.inch | Inside dia. ft | Cross area ft2
1.5" meter | 1.313 | 0.10942 | 0.0094028
2" meter | 1.75 | 0.14583 | 0.016703